Insulated Pipe Support Specifications

Materials and Workflow

MasterFormat© 2016 - Numbers and Titles

Applicable Reference Sections: (delete non-applicable sections)

- 22 07 19 - Plumbing Piping Insulation

- 23 05 29 - Hangers and Supports for HVAC Piping and Equipment

- 23 07 19 - HVAC Piping Insulation

- 23 21 16 - Hydronic Piping Specialties

- Pre-Insulated Pipe Supports

  - Mechanical Contractor shall install pre-insulated pipe supports at all structural hangers during the pipe installation process to ensure correct pipe elevations are set per plan.

  - Wood block inserts “notched” into pipe insulation shall not be allowed.

  - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

    - Thermal Pipe Shields

    - Insulation Components, Inc.

    - Pipe Shields, Inc.

    - Approved Equal

  - Basis of Design for all pipe diameters operating between 0 to 1200 °F

    - T-2000 Calsil manufactured by Thermal Pipe Shields

      - https://www.thermalpipeshields.com/product/t2000-calsil/

    - Insulation insert shall cover the entire circumference of the pipe and shall be fabricated from filter pressed, water resistant calcium silicate (calsil) per ASTM C533 type I with a factory laminated All Service Jacket (ASJ) vapor retarder meeting ASTM C1136 and a factory applied Self Sealing Lap (SSL) on the longitudinal joints.

    - Calsil shall have a minimum compressive strength of 200 psi per ASTM C165, minimum flexural strength of 80 psi per ASTM C203 and a flame spread and smoke developed of 0/0 per ASTM E84.

    - Calsil insert lengths shall be based upon pipe diameter on manufacturer’s published data sheet.

    - Insulated Pipe Support shall be covered by an integral two-piece 360-degree curved metal shield fabricated from G90 galvanized steel per ASTM A-527.  Lengths and gauge thicknesses based upon pipe diameter and hanger type as published on manufacturer’s product data sheet.

      - Insulation insert shall extend 1” beyond the metal shield on both sides to allow the adjacent mechanical insulation to be sealed with ASJ tape on the circumferential joints.

  - Contractor Voluntary Alternate for pipes operating below 200 °F.

    - F-2000 Phenolic manufactured by Thermal Pipe Shields

      - https://www.thermalpipeshields.com/product/f2000-phenolic/

    - Insulation insert shall cover the entire circumference of the pipe and shall be fabricated from phenolic foam per ASTM C1126 type III with a factory laminated All Service Jacket (ASJ) vapor retarder meeting ASTM C1136 and factory applied Self Sealing Lap (SSL) on the longitudinal joints.

    - Phenolic foam inserts lengths and densities shall be based upon pipe diameter on manufacturer’s published data sheet.

    - Insulated Pipe Support shall be covered by an integral two-piece 360-degree curved metal shield fabricated from G90 galvanized steel per ASTM A-527.  Lengths and gauge thicknesses based upon pipe diameter and hanger type as published on manufacturer’s product data sheet.

      - Insulation insert shall extend 1” beyond the metal shield on both sides to allow the adjacent mechanical insulation to be sealed with ASJ tape on the circumferential joints.

  - When installing pipe without a welded-on shoe-type support saddle (MSS SP-58 type 39) over Roller Style Hangers, mechanical contractor shall install 200 psi minimum calcium silicate insulated pipe support in manufacturer’s standard recommended length AND a secondary Type 40 curved metal shield in accordance with MSS SP-58 table A3:

    - 12” long x 18-gauge steel for 3 ½” and smaller pipes.

    - 12” long x 16-gauge steel for 4” pipes.

    - 18” long x 16-gauge steel for 5” to 6” pipes

    - 24” long x 14-gauge steel for 8” to 14” pipes

    - 24” long x 12-gauge steel for 16” to 24” pipes

      - Secondary metal shield shall be installed directly on the roller hanger and positioned to keep rolling point of contact within the middle one-third of the shield length.

End of Section